## Sheet1
Input Parameters for Foundation Design :-
| Sl.No | Description |  | Variable | Unit | Value
| 1 | 1st Slope of Tower Leg |  | F | Deg
| 2 | Depth of Soil Below G.L |  | Dl | m
| 3 | Unit Weight of Soil Below G.L |  | Ws | Kg/m3
| 4 | Angle of Repose |  | a | Deg
| 5 | Limit Bearing Capacity of Soil |  | Lbcs | Kg/m2
| 6 | Factor of Safety applied on foundation loads |  | Fos | --
| 7 | Total Depth of Foundation Below G.L (Including Pcc Pad) |  | D | m
| 8 | Plinth Height |  | Dp | m
| 9 | Unit Weight of Concrete below G.L |  | Wc | Kg/m3
| 10 | Characteristic Strength of Concrete |  | Fck | N/mm2
| 11 | Characteristic Strength of Steel |  | Fy | N/mm2
| 12 | Cover To Chimney Reinforcement |  | Ccc | mm
| 13 | Cover To Footing Slab Reinforcement |  | Ccs | mm
| 14 | Slope of Tower Leg |  | F | Deg
| 15 | Unit Weight of Concrete above ground level |  | Wdc | Kg/m3
Assumed Dimensions of Foundation Refer Figure- I
| 1 | Footing Width at the Bottom of Slab -I |  | B | m
| 2 | Footing Width At Bottom of Slab - II |  | B1 | m
| 3 | Footing Width At Top of Slab - II |  | B1 | m
| 4 | Width of Footing At Bottom of Slab - III |  | B2 | m
| 5 | Width of Footing At Bottom of Slab - IV |  | B3 | m
| 6 | Width of Chimney |  | Bc | m
| 7 | Depth of PCC Pad |  | Dpad | m
| 8 | Depth of Slab -I Fom top of PCC Pad |  | D1 | m
| 9 | Depth of Slab -II from top of Slab-I |  | D2 | m
| 10 | Depth of Slab -III from top of Slab-II |  | D3 | m
| 11 | Depth of Slab -IV from top of Slab-III |  | D4 | m
| 12 | Height of Chimney Upto G.L From Top of Slab - IV |  | Dc | m
Ultimate Foundation Loads in kg - Refer Doc. No. O19018-T-TL-0S-DC-0300
C+9M B.E
| Sr. No | Type of Load |  | CASE-1
| 1 | Compression
| 2 | Uplift
| 3 | Side Thrust (Transverse)
| 4 | Side Thrust (Longitudinal)
|  |  |  | Including Material strength factor of 1.02 | Without Material strength factor of 1.02
( 1 ) --- CHECK FOR UPLIFT (REFER FIGURE - 2)
Sr. No. | Description |  | Expression
(a) | Horizontal Offset of cone in Layer Below G.L
(b) | Gross volume of soil below G.L in M3
(c) | Volume of Concrete below G.L in M3 excluding bottom pad
(d) | Net Volume of soil below G.L in M3
(e) | Weight of Soil Resisting Uplift in Kg
(f) | Weight of Concrete in Kg
(g) | Total Resistance against Uplift in Kg
(h) | Factor of Safety against Uplift
Since F.O.S is > 1.00 , Foundation is Safe against Uplift
( 2 ) --- CHECK FOR DOWNTHRUST
(A) Bearing Pressure Due to Downthrust in Kg/m2
(a) | Downthrust acting perpendicular to footing (Y1)
(b) | Over Load due to Concrete (Kg)
(c) | Total Downthrust acting normal to footing in Kg
(d) | Bearing Pressure Due to Downthrust (Kg/m2) (P/A)
(e) | Depth of Slab below chimney in M
(f) | Moment Due to Eccentricity (MX & MZ)
(g) | Bearing Pressure Due to Eccentricity in Kg/m2 (Mx/Z)
(h) | Bearing Pressure Due to Eccentricity in Kg/m2 (Mx/Z+My/Z)
(i) | Total Bearing Pressure in Kg/m2
(j) | Factor of Safety against Bearing
Since F.O.S is > 1.00 , Foundation is Safe Against bearing
Sr. No. | Description |  | Expression |  |  |  | Value
(B) Bearing Pressure Due to Transverse Side Thrust in Kg/m2
(a) | Coefficient of Passive Earth Pressure (Kp)
(b) | Depth of Chimey above Slab-III
(c) | Depth of Effective earth pressure Zone (He) in M
(d) | Since Effective Pressure Zone (He) is < (2.8- 0.5) , Therefore Soil Pressure will only be mobilised in 1.391 m Depth
(e) | Resisting Soil Force in Kg (R) =
(f) | Moment @ Base Due to Side Thrust (Kg-m)
(g) | Bearing Pressure due to SideThrust in Kg/m2
(C) Bearing Pressure Due to Longitudinal Side Thrust in Kg/m2
(a) | Depth of Effective earth pressure Zone (He) in M
(b) | Since Effective Pressure Zone (He) is < (2.8- 0.5) , Therefore Soil Pressure will only be mobilised in 1.111 m Depth from the root of the chimney
(c) | Resisting Soil Force in Kg (R) =
(d) | Moment @ Base Due to Longitudinal Thrust (Kg-m)
(e) | Bearing Pressure due to Longitudinal Thrust in Kg/m2
(f) | Total Bearing Pressure due to Downthrust & Side Thrust in Kg/m2
(g) | Factor of Safety against Bearing
| (Limit bearing pressure is increased by 25% as per IS 4091-1979 cl 5.2) |  | Since F.O.S is >1.00, Foundation is Safe In Bearing
( 3) STRUCTURAL DESIGN OF FOUNDATION
A) | Design Base Slab Reinforcement
(Refer Fig-5 for base pressure distribution)
(a) | Design bearing pressure (Kg/m2)
(b) | Maximum , Pmax in Kg/m2
(c) | Minimum , Pmin in Kg/m2
(d) | Maximum pressure Pmax in N/mm2
(e) | Minimum pressure Pmin in N/mm2
(f) | Total Depth of At Section X-X in 'm'
(g) | Effective Depth of Slab (Dactual) at Section X-X in mm
(h) | Total Depth of At Section Y-Y in M
(i) | Effective Depth of Slab (Dactual) in mm
(j) | Total Depth of At Section Z-Z in M
(k) | Effective Depth of Slab (Dactual) in mm
(l) | Distance from the edge of the footing to Section X-X in 'm'
(m) | Distance from the edge of the footing to Section Y-Y in 'm'
(n) | Distance from the edge of the footing to Section Z-Z in 'm'
(o) | Pressure at a distanced=582mmfrom section X-X
(p) | Pressure at a distanced=382mmfrom section Y-Y
(q) | Pressure at a distanced=232mmfrom section Z-Z
(r) | The pressure at section X-X (Pxx in Kg/m2)
(s) | The pressure at section Y-Y (Pyy in Kg/m2)
(t) | The pressure at section Z-Z (Pyy in Kg/m2)
(u) | Bending Moment at face of chimney at Section X-X in kg-m per m width
(v) | Bending Moment at face of chimney at Section X-X in N-mm per m width
| No and Diameter of Bars to be used in Base Slab |  | No of Bars required for base slab |  | Diameter of Bar in mm |  | Area of Bars (Ast) in mm2
MKD "K"
Value of Xumax /d to be used in slab design
Effective Depth Required for slab (Dreqd) in mm
| Breadth at section -XX in M = 1.6 |  | Since (dreqd) < than (dactual), Slab depth is O.K
Moment of Resistance at Section - XX Mrx in N-mm
Total Reinforcement Ast required in mm2
where Ast = Reinforcement Reqd. for moment Mrx /m width
Ast required for total width
Minimum steel area required , mm2
(c) | Bending Moment about Section Y-Y per m width
Effective Depth Required for slab (Dreqd) in mm
| Breadth at section -YY in M = 3.1 |  | Since (dreqd) < than (dactual), Slab depth is O.K
(d) | Moment of Resistance at Section - YY Mry in N-mm
where Ast = Reinforcement Reqd. for moment Mry /m width
Ast required for total width
(f) | Minimum steel area required , mm2
(g) | Bending Moment about Section Z-Z per m width
Effective Depth Required for slab (Dreqd) in mm
| Breadth at section -ZZ in M = 5.57 |  | Since (dreqd) < than (dactual), Slab depth is O.K
(h) | Moment of Resistance at Section - ZZ Mry in N-mm
where Ast = Reinforcement Reqd. for moment Mry /m width
Ast required for total width
(i) | Minimum steel area required , mm2
Maximum of the above area of steel is provided as Slab Reinforcement
Total No of bars required for slab
| Hence the spcacing between rod is (mm) | [5 empty] | O.K.
B) | Check for One Way Shear At Section - XX : - (Refer Fig -3)
(a) | Shear At Section - XX per m run in N
(b) | Effective Area of Cross Section per m run in mm2
(c) | Nominal Shear Stress Tv in N/mm2 /m
(d) | Total Effective Area of Cross Section in mm2
(e) | Percentage Slab reinforcement (p)
(f) | Permissible Shear Stress Tc in N/mm2
(g) | Permissible Shear Stress Tc in N/mm2
(h) | Where Coefficient Ct is given by
(i) | Permissible Shear Stress Tc in N/mm2
( Since Tc (0.3706) > than Tv(0.214) Shear Reinforcement is not required )
C) | Check for One Way Shear At Section - YY : - (Refer Fig -3)
(a) | Shear At Section - YY per m run in N
(b) | Effective Area of Cross Section per m run in mm2
(c) | Nominal Shear Stress Tv in N/mm2 /m
(d) | Total Effective Area of Cross Section in mm2
(e) | Percentage Slab reinforcement (p)
(f) | Where Coefficient Ct is given by
(g) | Permissible Shear Stress Tc in N/mm2
( Since Tc (0.3971)> than Tv (0.288)Shear Reinforcement is not required )
D) | Check for One Way Shear At Section - ZZ : - (Refer Fig -3)
(a) | Shear At Section - ZZ N
(b) | Effective Area of Cross Section per m run in mm2
(c) | Nominal Shear Stress Tv in N/mm2 /m
(d) | Total Effective Area of Cross Section in mm2
(e) | Percentage Slab reinforcement (p)
(f) | Where Coefficient Ct is given by
(g) | Permissible Shear Stress Tc in N/mm2
( Since Tc(0.4499)> than Tv(0.302) Shear Reinforcement is not required)
E) | Check for Two Way Shear At Section - XX : - (Due to Downthrust) (Refer Fig -3)
(a) | Pressure at Section XX in N/mm2
(b) | Shear At Section - XX in N
(c) | Effective Area of Cross Section in mm2
(d) | Nominal Shear Stress Tv in N/mm2
Allowable Shear Stress (Tcmax) in N/mm2
Tcmax = Ks * Tc
(e) | Allowable Shear Stress in concrete (Tcmax) in N/mm2
( Since Tcmax(1.118) > than Tv(0.677) Shear Reinforcement is not required )
Sr. No. | Description |  | Expression |  |  |  | Value
F) | Check for Two Way Shear At Section - YY : - (Due to Downthrust) (Refer Fig -3)
(a) | Pressure at Section YY in N/mm2
(b) | Shear At Section - YY in N
(c) | Effective Area of Cross Section in mm2
(d) | Nominal Shear Stress Tv in N/mm2
(e) | Allowable Shear Stress in concrete (Tcmax) in N/mm2
( Since Tcmax(1.118) > than Tv(0.642) Shear Reinforcement is not required )
G) | Check for Two Way Shear At Section - ZZ : - (Due to Downthrust) (Refer Fig -3)
(a) | Pressure at Section ZZ in N/mm2
(b) | Shear At Section - ZZ in N
(c) | Effective Area of Cross Section in mm2
(d) | Nominal Shear Stress Tv in N/mm2
(e) | Allowable Shear Stress in concrete (Tcmax) in N/mm2
( Since Tcmax(1.118) > than Tv (0.798)Shear Reinforcement is not required )
H) | Design of Slab for Uplift Reinforcement at Section - ZZ : -
(ai) | Effective depth at section Z-Z in the view of uplift reinforcement
(bi) | Effective depth at section Y-Y in the view of uplift reinforcement
(ci) | Effective depth at section X-X in the view of uplift reinforcement
(a) | Bearing Pressure due to Uplift in Kg/m2
(a) | Bending Moment/m width @ - ZZ (Mux) in N-mm
(b) | Moment of Resistance at Section - ZZ Muy in N-mm
(c) | Astuy = Reinforcement for Uplift @ - ZZ /M-width
Minimum steel area required , mm2
(d) | No and Diameter of Bars to be used in Base Slab |  | Diameter of Bar in mm |  | No of Bars required for Uplift force @ ZZ
At Section - ZZ for Uplift Reinforcement
( Let us Provide 23 Nos of 12mm diameter rod as Uplift Reinforcement at Section - ZZ MKD, 'L' )
| Hence the spcacing between rod is (mm) | [5 empty] | O.K.
I) | Design of Slab for Uplift Reinforcement at Section - YY : -
It may be noted that reinforcement provided at section Z-Z for uplift falls in tension zone and thus would also contribute in moment capacity of section at
section Y-Y. This is because under uplift, compression occurs at the face of the base slab having more width (more area of compression flange) and section
behaves as a highly under reinforced section. From the equilibrium of internal and external forces on the slab section and using stress and strains of
concrete and steel as per IS:456, the following equation (Moment of resistance) can be obtained
Xu/d1 = (p3/100)x(d2/d1)x(fs/0.36fck) + (p4/100)x(0.87fy/0.36fck)
where:- p3 = (100 As3 / Bd2) and p4 = ( 100 As4/ Bd1); fs= Design yield stress of steel at d2 from MCE calculated for strain in steel at that level(arrived through interpolation from strain diagram)
As3 = Area of reinforcement at the top of bottom-most step, As4 = Area of reinforcement at the top of the topmost step
Moment of resistance of slab section at the face of the chimney:
Mu = [0.87fy * (p3/100) * (d2/d1) * (d2/d1 - 0.416 Xu/d1) + (0.87fy) * (p4/100) * (1-0.416Xu/d1)] * Bd12
Substituting the value of Xu/d1 in the above equation, we get the second order degree equation which can be resolve as follows:-
A = 0.416* (0.87*fy)^2/(0.36*fck)
B = 0.416*((0.87*fy)/(0.36*fck)) * ((fs*(p3/100)*(d2/d1)) + ((0.416*fs*(p3/100)*(d2/d1))*((0.87*fy)/(0.36*fck)) - 0.87*fy
C= (Mux/B*d1*d1) - (fs*(p3/100)*(d2/d1)^2) + (0.416*(p3/100)*(d2/d1)) * ((fs)/(0.36*fck))*((fs*(p3/100)*(d2/d1))
(a) | Bearing Pressure due to Uplift in Kg/m2
(b) | Bending Moment @ - YY (Mux) in N-mm
(c) | Strain in reinforcement at d2 from Bottom of slab-I (By linear interpolation from Strain Diagram)
(d) | Design yield stress of reinforcement at d2 from Bottom of slab-I (fs in N/mm2) [Refer Fig.3 of SP-16]
A = 0.416* (0.87*fy)^2/(0.36*fck)
B = 0.416*((0.87*fy)/(0.36*fck)) *((fs*(p3/100)*(d2/d1))
+ ((0.416*fs*(p3/100)*(d2/d1))*((0.87*fy)/(0.36*fck))
- 0.87*fy
C= (Muy/B*d1*d1) - (fs*(p3/100)*(d2/d1)^2)
+ (0.416*(p3/100)*(d2/d1)) * ((fs)/(0.36*fck))
*((fs*(p3/100)*(d2/d1))
Therefore by resolving the above equation, we get,
ps4/100
Therefore reinforcement Ast4 in mm2
(c) | No and Diameter of Bars to be used in Base Slab |  | Diameter of Bar in mm |  | No of Bars required for Uplift force @ YY
At Section - YY for Uplift Reinforcement
( Let us Provide 20 Nos of 12mm diameter rod as Uplift Reinforcement at Section - YY, MKD 'M')
| Hence the spcacing between rod is (mm) | [5 empty] | O.K.
J) | Design of Slab for Uplift Reinforcement at Section - XX : -
It may be noted that reinforcement provided at section Y-Y for uplift falls in tension zone and thus would also contribute in moment capacity of section at
section X-X. This is because under uplift, compression occurs at the face of the base slab having more width (more area of compression flange) and section
behaves as a highly under reinforced section. From the equilibrium of internal and external forces on the slab section and using stress and strains of
concrete and steel as per IS:456, the following equation (Moment of resistance) can be obtained
Xu/d1 = (p3/100)x(d2/d1)x(fs/0.36fck) + (p4/100)x(0.87fy/0.36fck)
where:- p3 = (100 As3 / Bd2) and p4 = ( 100 As4/ Bd1); fs= Design yield stress of steel at d2 from MCE calculated for strain in steel at that level(arrived through interpolation from strain diagram)
As3 = Area of reinforcement at the top of bottom-most step, As4 = Area of reinforcement at the top of the topmost step
Moment of resistance of slab section at the face of the chimney:
Mu = [0.87fy * (p3/100) * (d2/d1) * (d2/d1 - 0.416 Xu/d1) + (0.87fy) * (p4/100) * (1-0.416Xu/d1)] * Bd12
Substituting the value of Xu/d1 in the above equation, we get the second order degree equation which can be resolve as follows:-
A = 0.416* (0.87*fy)^2/(0.36*fck)
B = 0.416*((0.87*fy)/(0.36*fck)) * ((fs*(p3/100)*(d2/d1)) + ((0.416*fs*(p3/100)*(d2/d1))*((0.87*fy)/(0.36*fck)) - 0.87*fy
C= (Mux/B*d1*d1) - (fs*(p3/100)*(d2/d1)^2) + (0.416*(p3/100)*(d2/d1)) * ((fs)/(0.36*fck))*((fs*(p3/100)*(d2/d1))
(a) | Bearing Pressure due to Uplift in Kg/m2
(b) | Bending Moment @ - XX (Mux) in N-mm
(c) | Strain in reinforcement at d2 from Bottom of slab-I (By linear interpolation from Strain Diagram)
(d) | Design yield stress of reinforcement at d2 from Bottom of slab-I (fs in N/mm2) [Refer Fig.3 of SP-16]
A = 0.416* (0.87*fy)^2/(0.36*fck)
B = 0.416*((0.87*fy)/(0.36*fck)) *((fs*(p3/100)*(d2/d1))
+ ((0.416*fs*(p3/100)*(d2/d1))*((0.87*fy)/(0.36*fck))
- 0.87*fy
C= (Muy/B*d1*d1) - (fs*(p3/100)*(d2/d1)^2)
+ (0.416*(p3/100)*(d2/d1)) * ((fs)/(0.36*fck))
*((fs*(p3/100)*(d2/d1))
Therefore by resolving the above equation, we get,
ps4/100
Therefore reinforcement Ast4 in mm2
Minimum steel area required , mm2
(c) | No and Diameter of Bars to be used in Base Slab |  | Diameter of Bar in mm |  | No of Bars required for Uplift force @ XX
At Section - XX for Uplift Reinforcement
( Let us Provide 12 Nos of 12mm diameter rod as Uplift Reinforcement at Section - XX, MKD 'N')
| Hence the spcacing between rod is (mm) | [5 empty] | O.K.
( 4 ) CHECK FOR SLIDING (Refer Figure - 4)
Sr. No. | Description |  | Expression |  |  |  | Value
(a) | Coefficient of Passive Earth Pressure in Lower layer
(b) | Facial Area in Chimney in m2
(e) | Facial Area in Portion of Slab- IV in m2
(f) | Facial Area in Portion of Slab- III in m2
(g) | Facial Area in Portion of Slab- II in m2
(h) | Facial Area in Portion of Slab- I in m2
(j) | Earth Pressures in Layer 1 in Kg /m2
(k) | Earth Pressures in Lower Layer 2 in Kg /m2
(l) | Earth Pressures in Lower Layer 3 in Kg /m2
(m) | Earth Pressures in Lower Layer 4 in Kg /m2
(n) | Earth Pressures in Lower Layer 5 in Kg /m2
(p) | Lateral Force in Lower Layer -1 in Kg
(q) | Lateral Force in Lower Layer -2 in Kg
(r) | Lateral Force in Lower Layer -3 in Kg
(s) | Lateral Force in Lower Layer -4 in Kg
(t) | Lateral Force in Lower Layer -5 in Kg
Total Lateral Force in Kg
Factor of Safety Against Sliding : -
Since F.O.S >1.00 foundation is Safe against sliding
( 5 ) CHECK FOR OVERTURNING
Sr. No. | Description |  | Expression |  |  |  | Value
(a) | Maximum Transverse Side Thrust in Kg
(b) | Maximum Longidutinal Side Thrust in Kg
(c) | Resultant Side Thrust (R) in Kg
(d) | Total Overturning Moment in Kg-m
(e) | Total Resisting Moment in Kg-m
(f) | Factor of Safety Against Overturning
Since F.O.S >1.00 foundation is Safe against Overturning